## HOW TO USE
Solar Energy Decomissioning Calculator
Terms of use and disclaimer
This calculator is provided for use by the public including persons engaging in commercial activities.
No person or entity (including, without limitation, the State of New South Wales) associated with the development of the calculator makes any representation or warranty regarding its contents, or is liable for any loss or damage whatsoever that may result from the use of the template or any portion or variation thereof, or any other materials presented in conjunction with the calculator, or any errors or omissions in its contents.
Users of the calculator must exercise their own skill and judgment and should seek advice from a suitably qualified experts, where appropriate.
The outputs of the calculator are estimations only and subject to a range of variables that can and will change overtime.
How to use
This calculator contains a range of fields that can be modified to account for the individual aspects of a project. Other fields and information are locked to provide consistent estimations. Enter information into the 'CALCULATOR TAB' to determine an estimate.
Fields that can be modified are shown in blue

## CALCULATOR
| SOLAR DECOMMISSION INPUTS |  |  |  |  | SOLAR TRIGER
| SECTION | DESCRIPTION | UNIT | QUANTITY | COMMENT | DESCRIPTION | TRIGGER
|  | Overall Size of Solar Farm | MW | 250 | Input overall size of power Generation | Haul Road Removal | Yes | 1
| Panels | Development Footprint | ha | 895 |  | Underground Cable/Pit Removal | Yes | 1
|  | Number of Panels | each | 715000 |  | Silcon Recovery | Yes | 1
|  | Panel Weight | kg | 27 |  | Aluminium and Alloy Recovery | Yes | 1
|  | Area of Panels | ha | 269.8 |  | Copper and Alloy Recovery | Yes | 1
| Foundation | Foundation Type | Concrete Footing |  | Select foundationType | Polymer and Plastics Recovery | Yes | 1
|  | Footings | m3 | 45000 | It is assumed that size of the footing is 0.5m wide, 0.5m long and 1m deep | Glass Recovery | Yes | 1
|  | Number of Piles | each | 180000 |  | Silver Recovery | Yes | 1
| Cable/Pit | Quantity of Cable Per Panel | m | 2.2 |  | Residual Waste | Yes | 1
|  | Number of Conduits | each | 4 | It is assumed that there are 4 conduits and there is 150m of conduits for each PCU | Concrete Recovery | Yes | 1
|  | Length of Conduit | m/PCU | 150
|  | Pit Intervals | m | 250
| Access Track/Make Good | Access Track | m | 50000
|  | Access Track | m2 | 346500 | It is assumed that every PCU has 1100m of access road and the width is 7m
|  | Access Road Thickness | m | 0.15
|  | Topsoil | m2 | 349155
Yes | Building | Number of Buildings | each | 3
| Mechanical Section | PCU Panel Intervals | panels | 16000 | Every 16,000 panels has 1 PCU
|  | Area of PCU Concrete Slab | m2 | 2655 | The size size of a PCU is 12m long and 4m wide and the foundation size of a kiosk is 1.5m by 1.1m
|  | Thickness of PCU Concrete Slab | m | 0.25 | Assumed 250mm slab
|  | Steel Frames Quantity | tonne | 2430 | This item is for removing the steel frame. It is assumed that every 5m there is a column, beam and bracing
|  | Number of Kiosk | each | 300
| Recovery | Silcon Recovery | % | 8.5
|  | Aluminium and Alloy Recovery | % | 16
|  | Copper and Alloy Recovery | % | 2.4
|  | Polymer and Plastics Recovery | % | 4.5
|  | Glass Recovery | % | 60
|  | Silver Recovery | % | 0.1
|  | Residual Waste | % | 8.5
| Distances | Distance to Scrap | km | 450
|  | Distance to Landfill | km | 500
|  | Contractor Allowance for Margin and Overheads |  | 35%
|  | Risk/Contingency Allowance |  | 25%
SOLAR DECOMMISSION OUTPUTS
|  | DESCRIPTION | UNIT | AMOUNT | COMMENT
|  | Total Cost Exc Recovery | $ | 58518272.033
|  | Recovery of Material | $ | 18353375.25
|  | Total Cost After Recovery | $ | 40164896.783
|  | Cost Per Mega Watt Exc Recovery | $/MW | 234073.0881
|  | Cost Per Mega Watt Inc Recovery | $/MW | 160659.5871
|  | Cost Per Panel Exc Recovery | $/panel | 81.8437
|  | Cost Per Panel Inc Recovery | $/panel | 56.1747

## ASSUMPTIONS 1
DECOMMISSIONING OF WIND TURBINE DIRECT JOB COST
ITEM NO | DESCRIPTION | CREW | UNIT | QUANTITY | RATE PER UNIT | PRODUCTIVITY PER UNIT | DURATION (DAYS) | TOTAL AMOUNT ($) | COMMENT
1 | Disconnection of Site From Grid and De-energisation of Solar Plant | Electrical Works Total | each | 715000 | 3280 | 50000 | 15 | 49200 | Including removing fuses from cartridges and monitoring and data circuits
2 | Cable Removal | Cable Removal Crew | m | 1573000 | 3250 | 1500 | 104.9 | 340925 | Removal of 1500m cable per hr and it is assumed that there 2.2m of cable per panel
3 | Removal of PCU | Inverter Removal Crew | Each | 45 | 12220 | 2 | 23 | 281060 | Every 16,000 panels has 1 PCU
4 | Removal of Kiosk Inverter | Kiosk Removal Crew | Each | 300 | 5050 | 10 | 30 | 151500 | Every row has kiosk transformer and it is assumed that the length of the row is 1500m and spacing between rows is 6m. The size of each kiosk is 1mx0.6mx0.3m
5 | Removal of Solar Panels | Solar Crew | Each | 715000 | 6020 | 1250 | 572 | 3443440 | It is assumed that one crew can remove 1250 panels per day
|  | Solar Transport Crew | Each | 715000 | 4720 | 240 | 298 | 1406560
|  | T&D | tonne | 19305 | 175 | 8 | 8128.4211 | 1422473.6842 | Considering the size of the panels and the size of the semi-trailer. It seems that a semi can carry up to 700 panels and this is equivalent to 19tonne. It is assumed that panel weight is 27kg
|  | Solar Transport Crew | tonne | 2430 | 4720 | 48 | 50.625 | 238950 | This item is for removing the steel frame. It is assumed that every 5m there is a column, beam and bracing
|  | Steel Transport | tonne | 2430 | 175 |  | 810 | 141750 | It is assumed that 100mm C Section is used and the weight is around 3kg/m.
|  | Recovery of Steel | tonne | 2430 |  |  |  |  | It is assumed that every 5m there is a column, beam and bracing
|  | Recovery of Solar Panels | tonne | 19305
6 | Removal of Concrete Foundations | Concrete Crew Total | m3 | 663.75 | 6550 | 25 | 27 | 176850 | It is assumed that foundation thickness is 250mm. The size size of a PCU is 12m long and 4m wide and the foundation size of a kiosk is 1.5m by 1.1m
7 | Concrete Disposal | Concrete Disposal Crew | tonne | 1659.375 | 23400 | 150 | 12 | 280800
|  | Disposal Fee | tonne | 1659.375 | 40 |  |  | 66375
|  | Recovery Steel | tonne | 99.5625 |  |  |  |  | Assumed 150kg of steel per m3 of concrete
8 | Removal of Panel Foundations | Pile Removal Crew | Each | 0 | 2770 | 40 | 0 | 0 | It is assumed that every 5m there is a pile of two rows and this is the function of number of rows
|  | Concrete Crew Total | m3 | 45000 | 6550 | 25 | 180 | 1179000 | It is assumed that size of the footing is 0.5m wide, 0.5m long and 1m deep
|  | Pile Transport Crew | tonne | 0 | 7900 | 5 | 0 | 0 | It is assumed that 2m 100mm steel piles and the weight of each pile is 125kg. Hence a truck and dog can carry up to 208 piles
|  | Concrete Disposal Crew | tonne | 112500 | 23400 | 150 | 75 | 1755000 | It is assumed that size of the footing is 0.5m wide, 0.5m long and 1m deep
|  | Concrete Disposal Fee | tonne | 107100 | 40 |  |  | 4284000 | It is assumed that size of the footing is 0.5m wide, 0.5m long and 1m deep
|  | Recovery of Reo | tonne | 5400 |  |  |  |  | It is assumed that reo density is 120kg/m3
|  | Recovery of Piles | tonne | 0 |  |  |  |  | It is assumed that 2m 100mm steel piles and the wieght of each pile is 125kg
9 | Removal of Conduits | Conduit Crew Total | m | 6750 | 8400 | 20 | 33.75 | 283500 | It is assumed that there are 4 conduits and there is 150m of conduits for each PCU
|  | Pit Crew Total | Each | 27 | 8550 | 1 | 2.7 | 23085
|  | Conduit Disposal - T&D | m | 6750 | 175 |  | 16 | 2800 | One T&D can carry 750m of used conduit. Considering the distance total cycle time is around 8hr
|  | Disposal Fee - Conduit | tonne | 21060 | 65 |  |  | 1368900 | The weight of 50mm conduit per m is around 0.78kg and it is assumed that there 4 conduits to be removed
|  | Disposal Fee - Concrete | tonne | 27 | 40 |  |  | 1080
10 | Removal of Access Road | Road/Crane Pad Crew | m2 | 346500 | 9850 | 120 | 288.8 | 2844680 | It is assumed that every PCU has 1100m of access road and the width is 7m
|  | Road Material Disposal | m3 | 51975 | 28650 | 30 | 173.3 | 4965045 | Assumed 150mm thick formation
|  | Disposal Fee | tonne | 93555 | 60 |  |  | 5613300
11 | Removal of Buildings | Building Crew | Each | 1 | 9500 | 20 | 20 | 190000
|  | Concrete Disposal Crew | tonne | 150 | 23400 | 150 | 1 | 23400 | Assumed 3 buildings
|  | Dispsoal Fee | tonne | 150 | 300 |  |  | 45000
12 | Removal of Fencing | General Civil Crew | m | 11966.6202 | 4800 | 500 | 23.9332 | 114879.5543 | Mass of fence 3kg/m2
12 | Topsoiling | Topsoil Crew | m2 | 349155 | 6550 | 150 | 232.77 | 1524643.5
13 | Mobilisation | Plant & Equipment | % | 1.5 |  |  |  | 483272.9511
13 | Disposal @ Landfill | Disposal Fee | tonne |  |  |  |  | 0
TOTAL DIRECT JOB COST | [7 empty] | 32701469.6896
`
`
ITEM NO | DESCRIPTION | UNIT | QUANTITY | RATE |  |  |  | AMOUNT | COMMENT
1 | Establishment of Environmental Protection | m | 106000 | 7.5 |  |  |  | 795000
2 | Maintenance of Environmental Protection | week | 45 | 1500 |  |  |  | 67500 | Duration is assumed to be around 45weeks
3 | Construction of Site Office Establishment | LS | 1 | 200000 |  |  |  | 200000
3 | Construction of Site Office Demob | LS | 0.33 | 200000 |  |  |  | 66000
3 | Construction of Site Office recurring cost | week | 45 | 15000 |  |  |  | 675000 | 10000 recurring costs
4 | Traffic Management | LS | 0.5% | 34504969.6896 |  |  |  | 172524.8484 | 0.5% of Base Estimate
TOTAL INDIRECT JOB COST | [7 empty] | 1976024.8484
[7 empty] | Subtotal | 34677494.5381
[7 empty] | Uplift Margin & Overheads | 12137123.0883
46814617.6264
[7 empty] | Risk Allowance/Contingency | 11703654.4066
58518272.033
| RECOVERY OF MATERIALS |  | UNIT | QUANTITY | RATE |  | Recovery | AMOUNT |  | Material type | Proportion of Solar Panel Mass | Assumed pathway is to^^: | Illustrative scrap value ($/tonne) ##
| Silcon |  | tonne | 5255.679 | 1000 |  | 1 | 5255679 |  | Silcon | 8.5% | Scrap metal facility | 1000
| Aluminium and alloys |  | tonne | 3088.8 | 1000 |  | 1 | 3088800 |  | Aluminium and alloys | 16% | Scrap metal facility | 1000
| Copper and alloys |  | tonne | 463.32 | 5000 |  | 1 | 2316600 |  | Copper and alloys | 2.4% | Scrap metal facility | 5000
| Polymer and Plastics |  | tonne | 868.725 | 100 |  | 1 | 86872.5 |  | Polymer and Plastics | 4.5% | Scrap metal facility | 100
| Glass (combination of cullet & fines) |  | tonne | 11583 | 30 |  | 1 | 347490 |  | Glass (combination of cullet & fines) | 60% | Scrap metal facility | 30
| Silver |  | tonne | 19.305 | 250000 |  | 1 | 4826250 |  | Silver | 0.1% | Scrap metal facility | 250000
| Steel |  | tonne | 2529.5625 | 100 |  | 1 | 252956.25 |  | Residual Waste | 8.5% | Landfill | 300
| Concrete |  | tonne | 108936.375 | 20 |  | 1 | 2178727.5 |  | Overall | 100%
^^ for material sent to landfill, assume a landfill disposal cost of $300/tonne
[7 empty] | Total Recovery | 18353375.25 |  | ## assumed scrap values are likely to be conservative
** for the concrete foundations, assume all material is sent to a recovery facility – scrap value is $20/tonne
[7 empty] | Price Inc Recovery | 40164896.783

## ASSUMPTIONS 2
LABOUR RATES USED |  |  |  | CREW RATES PER DAY
DESCRIPTION | UNIT | RATE | COMMENT | DESCRIPTION | INCLUSION | UNIT | QTY | RATE | TOTAL RATE PER DAY | COMMENT
LAB-CW2 | HR | 65 | General Labour | Electrical Works | LAB-CW5 | hr | 40 | 82 | 3280 | 2 man crew
LAB-CW3 |  | 75 | Fitter | Electrical Works Total |  |  |  |  | 3280
LAB-CW5 |  | 82 | Qualified Trade
LAB-CW6 |  | 86 | Operator | Excavator | Excavator 30T | hr | 10 | 175 | 1750
Liquid Waste Specialist |  | 110 | Liquid Waste Specialist | Concrete Breaker | Hammer 30T | hr | 10 | 20 | 200
|  |  |  | Tipper | Tipper 20T | hr | 20 | 150 | 3000 | Taking the concrete to site stockpile
Hours Per Day | hr | 10 |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300 | 2man crew
|  |  |  | Tools | Small Tools | hr | 20 | 15 | 300
|  |  |  | Concrete Crew Total |  |  |  |  | 6550
PLANT RATES USED
DESCRIPTION | UNIT | RATE | COMMENT | Excavator | Excavator 20T | hr | 10 | 160 | 1600
Excavator 30T | hr | 175 |  | Tipper | Tipper 20T | hr | 20 | 150 | 3000 | Taking the concrete to site stockpile
Excavator 20T | hr | 160 |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300 | 2man crew
Bobcat | hr | 135 |  | Roller | Roller 15-20T | hr | 10 | 120 | 1200
Attachment | day | 120 |  | Watercart | Watercart 12-15KL | hr | 10 | 130 | 1300
Tipper 20T | hr | 150
Roller 15-20T | hr | 120 |  | Conduit Crew Total |  |  |  |  | 8400
Watercart 12-15KL | hr | 130
Grader 140 | hr | 210 |  | Excavator | Excavator 20T | hr | 10 | 160 | 1600
Small Tools | hr | 15 |  | Tipper | Tipper 20T | hr | 20 | 150 | 3000 | Taking the concrete to site stockpile
Franna 25T | hr | 300 |  | Grader | Grader 140 | hr | 10 | 210 | 2100
Telehandler | day | 420 |  | Roller | Roller 15-20T | hr | 10 | 120 | 1200
Mobile 200T | hr | 850 |  | Watercart | Watercart 12-15KL | hr | 10 | 130 | 1300
Mobile 150T | hr | 750 |  | Labour | LAB-CW2 | hr | 10 | 65 | 650
Hammer 30T | day | 200 |  | Road/Crane Pad Crew |  |  |  |  | 9850
T&D | hr | 175
Hammer 20T | day | 150 |  | Excavator | Excavator 30T | hr | 10 | 175 | 1750
Oxy Cutter | hr | 12 |  | Concrete Breaker/Grabs | Hammer 30T | hr | 10 | 200 | 2000
|  |  |  | Tipper | Tipper 20T | hr | 20 | 150 | 3000
NO TRUCKS CONCRETE DISPOSAL |  |  |  | Labour | LAB-CW2 | hr | 40 | 65 | 2600 | 4man crew
Distance | km | 450 |  | Tools | Small Tools | hr | 10 | 15 | 150
Speed | km/hr | 80 |  | Building Crew |  |  |  |  | 9500
T&D Capacity | tonne | 30
Concrete Loading PR | m3/hr | 15 |  | Main Crane | Franna 25T | hr | 0 | 300 | 0 | Rates to be confirmed
Loading Time | min | 66.6667 |  | Telehandler | Telehandler | day | 10 | 42 | 420
Haulage Time | min | 675 |  | Rigger | LAB-CW3 | hr | 40 | 75 | 3000 | 6man crew
Unloading | min | 10 |  | Labour | LAB-CW2 | hr | 40 | 65 | 2600 | 2man crew
Change Trucks | min | 1.2 |  | Solar Crew |  |  |  |  | 6020
Total Cycle Time | min | 752.8667
Number of Trucks | each | 12 |  | Truck | T&D | hr | 120 | 175 | 21000
|  |  |  | Excavator | Excavator 30T | hr | 10 | 175 | 1750 | Per day PR is 30x10=300m3. Hence one excavator can load up to 750tonne/30 = 25 trucks
|  |  |  | Labour | LAB-CW2 | hr | 10 | 65 | 650
NO TRUCKS ROAD MATERIAL DISPOSAL |  |  |  | Concrete Disposal Crew |  |  |  |  | 23400
Distance | km | 450
Speed | km/hr | 80 |  | Truck | T&D | hr | 150 | 175 | 26250
T&D Capacity | tonne | 30 |  | Excavator | Excavator 30T | hr | 10 | 175 | 1750 | Per day PR is 75m3/hr x 10hr =750m3 per day. Hence one excavator can load up to 1350tonne/30 = 45 T&D
Loading PR | m3/hr | 20 |  | Labour | LAB-CW2 | hr | 10 | 65 | 650
Loading Time | min | 50 |  | Road Material Disposal |  |  |  |  | 28650
Haulage Time | min | 675
Unloading | min | 10 |  | Excavator | Excavator 20T | hr | 10 | 160 | 1600
Change Trucks | min | 1.2 |  | Tipper | Tipper 20T | hr | 20 | 150 | 3000
Total Cycle Time | min | 736.2 |  | Watecart | Watercart 12-15KL | hr | 10 | 130 | 1300
Number of Trucks | each | 15 |  | Labour | LAB-CW2 | hr | 10 | 65 | 650
|  |  |  | Topsoil Crew |  |  |  |  | 6550
NO TRUCKS PILE DISPOSAL |  |  |  | Fitter | LAB-CW3 | hr | 20 | 75 | 1500 | 2man crew
Distance | km | 450 |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300 | 2man crew
Speed | km/hr | 80 |  | Tools | Small Tools | hr | 30 | 15 | 450
T&D Capacity | tonne | 30 |  | Cable Removal Crew |  |  |  |  | 3250
Pile Loading PR | ton/hr | 5
Loading Time | min | 360 |  | Excavator | Excavator 20T | hr | 10 | 160 | 1600
Haulage Time | min | 675 |  | Hammer | Hammer 20T | hr | 10 | 15 | 150
Unloading | min | 10 |  | Tipper | Tipper 20T | hr | 20 | 150 | 3000
Change Trucks | min | 1.2 |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300
Total Cycle Time | min | 1046.2 |  | Roller | Roller 15-20T | hr | 10 | 120 | 1200
Number of Trucks | each | 3 |  | Watercart | Watercart 12-15KL | hr | 10 | 130 | 1300
|  |  |  | Pit Crew Total |  |  |  |  | 8550
Drive Steel Pile |  |  |  | Crane | Mobile 150T | hr | 10 | 750 | 7500
Concrete Footing |  |  |  | Telehandler | Telehandler | day | 10 | 42 | 420 | 4man crew
|  |  |  | Rigger | LAB-CW3 | hr | 40 | 75 | 3000 | 2man crew
|  |  |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300
TYPE OF FOUNDATION |  |  |  | Inverter Removal Crew |  |  |  |  | 12220
Concrete Footing | 0
|  |  |  | Crane | Franna 25T | hr | 10 | 300 | 3000
Recovery | Yes |  |  | Rigger | LAB-CW3 | hr | 10 | 75 | 750 | 2man crew
| No |  |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300
|  |  |  | Kiosk Removal Crew |  |  |  |  | 5050
|  |  |  | Bobcat | Bobcat | hr | 10 | 135 | 1350
|  |  |  | Attachment | Attachment | hr | 10 | 12 | 120 | 2man crew
|  |  |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300
|  |  |  | Pile Removal Crew |  |  |  |  | 2770
|  |  |  | Bobcat | Bobcat | hr | 10 | 135 | 1350 | It is assumed that 2m 100mm steel piles and the wieght of each pile is 125kg. Hence a truck and dog can carry up to 208 piles
|  |  |  | T&D | T&D | hr | 30 | 175 | 5250
|  |  |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300
|  |  |  | Pile Transport Crew |  |  |  |  | 7900
|  |  |  | Telehandler | Telehandler | day | 10 | 42 | 420
|  |  |  | Franna | Franna 25T | hr | 10 | 300 | 3000
|  |  |  | Labour | LAB-CW2 | hr | 20 | 65 | 1300
|  |  |  | Solar Transport Crew |  |  |  |  | 4720
|  |  |  | Bobcat | Bobcat | hr | 10 | 135 | 1350 | removal @ 500m per day
|  |  |  | Tipper | Tipper 20T | hr | 10 | 150 | 1500
|  |  |  | Labour | LAB-CW2 | hr | 30 | 65 | 1950 | 3 man crew
|  |  |  | General Civil Crew |  |  |  |  | 4800